## Page 1 - PART I, II
SMCMUA - Meter Sizing Application
Directions: Fill in white boxes with information requested.
PART I - General Information
Hydrant Test Information:
Static Pressure (psi)
Residual Pressure (psi)
Note: The hydrant flow test request form is included on the SMCMUA Engineering webpage.
PART II - Domestic Demand (Continuous)1
Fixture Type (standardized at 60 psi) | Fixture value (gpm) |  | Number of Fixtures |  | Total Fixture Value (gpm)
Toilet Tank Type | 4 | x |  | = | 0
Toilet Flush Valve | 35 | x |  | = | 0
Urinal (wall or stall) | 16 | x |  | = | 0
Urinal (flush valve) | 35 | x |  | = | 0
Urinal Trough (2 ft. unit) | 2 | x |  | = | 0
Bidet | 2 | x |  | = | 0
Shower Head (shower only) | 2.5 | x |  | = | 0
Bathtub | 8 | x |  | = | 0
Faucet (lavatory) | 1.5 | x |  | = | 0
Faucet (kitchen sink) | 2.2 | x |  | = | 0
Dishwasher | 2 | x |  | = | 0
Faucet (utility sink) | 4 | x |  | = | 0
Clothes Washer | 6 | x |  | = | 0
Hose (50 ft Wash Down):
1/2" connection | 5 | x |  | = | 0
5/8" connection | 9 | x |  | = | 0
3/4" connection | 12 | x |  | = | 0
Miscellaneous:
Bedpan Washers | 10 | x |  | = | 0
Dental Unit | 2 | x |  | = | 0
Drinking Fountain (public) | 2 | x |  | = | 0
Other Fixtures (include Description and values):
|  | x |  | = | 0
|  | x |  | = | 0
|  | x |  | = | 0
|  | x |  | = | 0
|  |  |  | = | 0
Total Fixture Value |  |  |  | = | 0
Water Flow Demand per fixture value (Refer to Figures 1 and 2, Page 2) gpm |  |  |  | =
Pressure adjustment factor (Refer to Table 1 on Page 7) |  |  |  | =
Water Flow Demand x Pressure Factor gpm |  |  |  | = | 0
Total Domestic Demand gpm |  |  |  | = | 0
1. American Water Works Association M22 2nd Ed.

## Page 2 - Reference Figures
SMCMUA - Meter Sizing Application
Figure 1: Water Flow Demand per Fixture Value – Low Range
Figure 2: Water Flow Demand per Fixture Value – High Range

## Page 3 - PART III, IV
SMCMUA - Meter Sizing Application
PART III - Irrigation Demand (Intermittent)1
| Area (100 Sq Ft) |  | Factor |  | Fixture Value (gpm)
Irrigated Area with SPRAY Systems |  | x | 1.16 | = | 0
Irrigated Area with ROTARY Systems |  | x | 0.4 | = | 0
Number of Hose Bibs |  | x | 6.5 | = | 0
Sub-Total Irrigation Demand (Irrigation + Hose Bib) gpm |  |  |  | = | 0
Pressure adjustment factor (Refer to Table 1, Page 7) |  |  |  | =
Sub-Total Irrigation Demand x Pressure Factor gpm |  |  |  | = | 0
Total Fixed Demands (if any) gpm |  |  |  | =
Total Irrigation Demand gpm |  |  |  | = | 0
PART IV - Mechanical Demand (Continuous or Intermittent)
Total Continuous Mechanical Demand* gpm |  |  |  | =
Total Intermittent Mechanical Demand* gpm |  |  |  | =
*Mechanical water demand refers to the intermittent and/or continuous operation of process equipment, cooling towers, A/C systems, wash down systems, etc. It is the responsibility of the designer to determine the demand values based on type of equipment and usage.

## Page 4- PART V
SMCMUA - Meter Sizing Application
PART V - Fire Demand - If Required (Intermittent)
1. Are hydrant(s) proposed onsite? |  | □ No | □ Yes, No. proposed
2. Does the building have automatic fire sprinklers? |  | □ No | □ Yes
3. Does the building require a fire pump? |  | □ No | □ Yes
Actual Fire Flow Demand (Per NFPA requirements) gpm |  |  |  | =
Pump Test Demand (if required, 150% of actual demand) gpm |  |  |  | = | 0
If you answered Yes to Questions 1, 2, or 3, proceed to question 4, otherwise skip to PART VI.
4. Requested Fire Service Lateral Size* |  | in
*Refer to Table 2 below. The velocity in the lateral must be ≤ 15 fps.
Table 2 - Fire Service Lateral Velocity Check
Fire Service Lateral Diameter (in) | Fire Service Lateral Area (sf) | Flow Rate thru Fire Lateral* (gpm) | Flow Rate thru Fire Lateral (cfs) | V (fps) = Q (cfs)/A (sf)
2" diameter | 0.021893 | 350 | 0.77 | 35.1713
3" diameter | 0.049063 | 350 | 0.77 | 15.6943
4" diameter | 0.087048 | 350 | 0.77 | 8.8457
6" diameter | 0.19625 | 350 | 0.77 | 3.9236
8" diameter | 0.34924 | 350 | 0.77 | 2.2048
10" diameter | 0.5447 | 350 | 0.77 | 1.4136
12" diameter | 0.785 | 350 | 0.77 | 0.98089
*If NO fire pump is required - use the actual fire flow demand per NFPA requirements in this entire column. If a fire pump IS required - use the pump test demand in this column. The pipe size that returns a velocity less than 15 fps is the target pipe size for the fire service.

## Pages 5-6 - PART VI
SMCMUA - Meter Sizing Application
PART VI - Meter Selection
If you answered YES to any of the questions in Part V, skip to #2 below.
1. Based on your answers, a single service connection will be made, and the meter should be sized based on the following flow rates:
1a. Normal Operating Demand = Domestic + Mechanical (cont.) gpm = |  |  | 0 | gpm
1b. Total Flow Thru Meter = Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.) = |  |  | 0 | gpm
Refer to Tables 3 and 4 on Page 6. The flow shown in 1a should be within 10% of the normal operating range. If the flow in 1b > 1a, the flow shown in 1b should between the normal operating range. Select the smallest meter that meets both criteria. The designer is responsible for ensuring the system is designed to accommodate headlosses imposed by the meter selected.
Requested Meter Type
Requested Meter Size
If your meter is sized smaller or larger than recommended please provide an explanation.
Thank You - this concludes your application
2. If you answered Yes to Question #1 of Part V, skip to #3 below.
Based on your answers, two service lines are required. One wet cut to the distribution system will be made. From the connection to the distribution system, two service connections are required: one for fire service and the other for domestic. A detector check valve or fire meter must be placed on the fire service line. Based on the information you provided, the domestic meter should be sized based on the following flows:
2a. Normal Operating Demand = Domestic + Mechanical (cont.) gpm = |  |  | 0 | gpm
2b. Total Flow Thru Meter = Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.) = |  |  | 0 | gpm
Refer to Tables 3 and 4 on Page 7. The flow shown in 2a should be within the normal operating range. The flow shown in 2b should be be less than or equal to the maximum intermittent flow. Select the smallest meter that meets both criteria. The designer is responsible for ensuring the system is designed to accommodate headlosses imposed by the meter selected.
Requested Meter Type
Requested Meter (Domestic) Size
| Lateral Size (in) (From Part V) | 0
Requested Fire Line Metering Device
Requested Wet Cut Size
If your meter is sized smaller or larger than recommended please provide an explanation.
Thank You - this concludes your application
3. How will the typical flow be characterized?
a. Light-domestic type use (generally characterized in Part II of this application) --------------------------> |  |  |  | Proceed to #4 Below
b. Higher Industrial/commercial flow (mostly characterized by Parts III and IV of this application) ------------> |  |  |  | Proceed to #5 Below
4. Based on your answers, two service lines are required. One wet cut to the distribution system will be made. From the connection to the distribution system, two service connections are required: one for fire service and the other for domestic. A fire meter must be placed on the fire service line. Based on the information you provided, the domestic meter should be sized based on the following flows:
4a. Normal Operating Demand = Domestic + Mechanical (cont.) gpm = |  |  | 0 | gpm
4b. Total Flow Thru Meter = Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.) = |  |  | 0 | gpm
Refer to Tables 3 and 4 on Page 7. The flow shown in 4a should be within the normal operating range. The flow shown in 4b should between less than or equal to the maximum intermittent flow. Select the smallest meter that meets both criteria. The designer is responsible for ensuring the system is designed to accommodate headlosses imposed by the meter selected.
Requested Meter Type
Requested Meter (Domestic) Size
| Lateral Size (in) (From Part V) | 0
Requested Wet Cut Size
If your meter is sized smaller or larger than recommended please provide an explanation.
Thank You - this concludes your application
5. Based on your answers, you have the option of having two service lines (fire and domestic), each with a meter, or using the HP Protectus meter. Under either circumstance, one wet cut to the distribution system will be made and the split for two service lines (if applicable) shall occur after the wet cut. Based on the information you provided, the meter should be sized based on the following flows:
5a. Normal Operating Demand = Domestic + Mechanical (cont.) gpm = |  |  | 0 | gpm
5b. Total Flow Thru Meter = Domestic + Irrigation + Mechanical (cont.) + Mechanical (inter.) = |  |  | 0 | gpm
5c. Fire Flow= |  |  | 0 | gpm
Refer to Tables 3 - 6 on Page 7. The flow shown in 5a should bewithin the normal operating range. If a separate domestic meter is chosen, the flow shown in 5b should be less than or equal to the maximum intermittent flow. If the HP Protectus meter is chosen, the maximum fire flow rate shown in 5c should be less than or equal to the maximum intermittent flow rate. Select the smallest meter that meets all criteria. The designer is responsible for ensuring the system is designed to accommodate headlosses imposed by the meter selected.
Requested Meter Type
Requested Meter Size
| Lateral Size (in) (From Part V) | 0
| Requested Fire Line Metering Device | HP Turbine Fire Service Meter
Requested Wet Cut Size
If your meter is sized smaller or larger than recommended please provide an explanation.
Thank You - this concludes your application

## Page 7 - Reference Tables
SMCMUA - Meter Sizing Application
Table 1 - Pressure adjustment factors
Working Pressure at Meter Discharge (psi) | Pressure Adjustment Factor
35 - 39 | 0.74
40 - 49 | 0.8
50 - 59 | 0.9
60 - 69 | 1
70 - 79 | 1.09
80 - 89 | 1.17
90 - 99 | 1.25
100 + | 1.34
Table 3 - Neptune T-10 Meter or Approved Equal
Meter Size | Low Flow Registration | Normal Operating Range (gpm) | Recommended Max Rate for Continuous Operations (gpm) | Maximum Intermittent Flow (gpm)
5/8" & 5/8" x 3/4 | 0.125 | 0.5 - 20 | 10 | n/a
3/4" | 0.25 | 0.75 - 30 | 15 | n/a
1" | 0.25 | 1 - 50 | 25 | n/a
1 1/2" | 0.375 | 2 - 100 | 50 | n/a
2"* | 1 | 2.5 - 160 | 80 | n/a
Table 4 - Neptune Tru/Flo Compound Meters or Approved Equal
Meter Size | Low Flow Registration | Normal Operating Range (gpm) | Maximum Intermittent Flow (gpm)
2" | 0.125 | 0.5 - 200 | 200
3" | 0.125 | 0.5 - 450 | 450
4" | 0.5 | 1 - 1000 | 1000
6" | 0.75 | 1 1/2 - 2000 | 2000
6" x 8" | 0.75 | 1 1/2 -2000 | 2000
Table 5 - Neptune HP Protectus Meter or Approved Equal
Meter Size | Low Flow Registration | Normal Operating Range (gpm) | Maximum Intermittent Flow (gpm)
4" | n/a | 0.75 -1200 | 1500
6" | n/a | 1.5 - 2500 | 3100
8" | n/a | 2 - 4000 | 5000
10" | n/a | 2 - 6500 | 8000
Table 6 - Neptune HP Turbine Meter or Approved Equal
Meter Size | Low Flow Registration | Normal Operating Range (gpm) | Maximum Intermittent Flow (gpm)
1 1/2" | n/a | 4 - 160 | 200
2" | n/a | 4 - 200 | 250
3" | n/a | 5 - 450 | 560
4" | n/a | 10 - 1200 | 1500
6" | n/a | 20 - 2500 | 3100
8" | n/a | 35 - 4000 | 5000
10" | n/a | 50 - 6500 | 8000
12" | n/a | 120 - 8000 | 10000

## DropDownMenus-DONOTEDIT (hidden)
Tru/Flo Compound | 5/8" | Tru/Flo Compound | 5/8" | Detector Check | HP Protectus
T-10 | 5/8" x 3/4 | T-10 | 5/8" x 3/4 | Fire Meter | Tru/Flow Compound
Other (Please specify) | 3/4" | HP Turbine Meter | 3/4" |  | HP Turbine Meter
| 1" | Other (Please specify) | 1"
| 1 1/2" |  | 1 1/2"
| 2" |  | 2"
| 3" |  | 3"
| 4" |  | 4"
| 6" |  | 6"
| 6" x 8" |  | 6" x 8"
8"
10"
Other (please specify)